ENERGY REGULATORY OFFICE

DEPARTMENT OF ENERGY ENTERPRISES

###### INFORMATION PACKAGE (RES)

FOR COMPANIES INTENDING TO CONDUCT BUSINESS ACTIVITIES IN THE FORM OF GENERATING ELECTRIC POWER IN

RENEWABLE ENERGY SOURCES (RES)

Exhibit 2. Requirements for metering and accounting systems and preparing the device installation description and chart

WARSAW, February 2010

Technical requirements for grid connection of generating equipment (and also electric energy distribution networks, final recipient equipment, intersystem connections and direct lines) were set forth in the regulation issued by the Minister of Economy dated 4 May 2007 on the detailed conditions for the operation of the electric power system (Journal of Laws of 2007, № 93, item 623, as amended) following Article 9 sections 3 and 4 of Energy Law Act, hereinafter referred to as system regulation.

In turn, the regulation issued by the Minister of Economy dated 14 August 2008, on the specific scope of the obligation to obtain and submit certificates of origin for redemption, payment of a replacement fee, purchase of electric energy and heat generated from renewable energy sources and the obligation to confirm the data concerning the amount of electric energy generated in renewable sources of electric energy (Journal of Laws of 2008, № 156, item 969), hereinafter referred to also as the RES regulation, defines, without limitation:

- Requirements on metering, registering and the manner of calculating the amount of electric energy or heat produced from renewable energy sources with installations, which in the process of generating energy uses an energy source referred to in Article 3 point 20 of the Energy Law Act dated 10 April 1997, hereinafter referred to as the Act, and other fuels;

- The location for taking readings of the amount of electric energy generated from renewable energy sources in compliance with the requirement of confirming the data referred to in Article 9e section 5 of the Act;

Under the system regulation, technical requirements for connecting generating equipment to the grid have been divided into the following two groups (designated as in the regulation):

- Technical requirements for connecting to the grid generating equipment, electric energy distribution networks, final recipient equipment, intersystem connections and direct lines of entities classified as Connector Groups I and II

- Technical requirements for connecting to the grid generating equipment, distribution networks, final recipient equipment, intersystem connections and direct lines of entities classified as Connector Groups III, IV, V and VI.

With respect to the above Group I, the requirements cover:

- General questions

- Technical requirements for equipment, installations and network of electric energy recipients

- Technical requirements for equipment, installations and network of electric energy producers

- Technical requirements for telecommunications and exchange of information systems

- Technical requirements for electric energy metering and accounting systems

- Technical requirements for metering and accounting systems

- Technical requirements for electric energy automatic protection systems and auxiliary devices

Technical requirements for electric energy metering and accounting systems (point 5) are as follows:

5.1. 	Network with rated voltage of 110 kV or higher, as well as equipment, installations and networks connected to the network with rated voltage of 110 kV or higher are to be equipped with electric energy metering and accounting systems capable of performing at least the function of measuring active and passive energy in two directions.

5.2. 	Technical requirements for electric energy metering and accounting systems are defined with respect to the systems, for which the measured amounts of electric energy serve as the basis for accounting and confirming such amounts of energy generated from renewable energy sources.

5.3. 	Technical solutions for electric energy metering and accounting systems depend on the rated power of the connected device, installation or network. These systems fall in three categories:

1)  category 1 – for measuring electric energy with device power rating of 30 MVA or higher;

2) category 2 – for measuring electric energy with device power rating ranging from 1 MVA to 30 MVA;

3)  category 3 – for measuring electric energy with device power rating of less than 1 MVA.

5.4.	Category 1 electric energy metering and accounting systems should meet the following requirements:

1)  current and voltage transformers in metering and accounting systems should have two cores and two measurement windings of precision class 0.2 for metering electric energy;

2)  electric energy meters in metering and accounting systems should be of precision class not less than 0.2 for active energy and 1 for passive energy;

3)   electric energy meters should be capable of working with automated data recording systems.

5.5. Category 2 electric energy metering and accounting systems should meet the following requirements:

1)   current and voltage transformers should be of precision class not less than 0.5;

2)   electric energy meters in metering and accounting systems should be of precision class not less than 0.5 for active energy and 3 for passive energy;

3)   electric energy meters should be capable of working with automated data recording systems.

5.6. Category 3 electric energy metering and accounting systems should meet the following requirements:

1)   current and voltage transformers should be of precision class not less than 0.5;

2)   electric energy meters in metering and accounting systems should be of precision class not less than 1 for active energy and 3 for passive energy;

3)   electric energy meters should be capable of working with automated data recording systems.

5.7. For categories 1 and 2 electric energy metering and accounting systems require two equivalent measuring systems: a main electric energy metering and accounting system and a back-up system.

5.8.	The back-up electric energy metering and accounting system is considered equivalent, when:

1)   for category 1 – electric energy meters in the main and back-up electric energy metering and accounting systems are powered from separate cores/windings of transformers installed in the same location, and the main and back-up electric energy metering and accounting systems meet the technical requirements set forth in point 5.4 of this Exhibit;

2)   for category 2 - the main and back-up electric energy metering and accounting systems meet the technical requirements set forth in point 5.5 of this Exhibit.

(…)

5.10 Electric energy metering and accounting systems should be installed:

1) on the side of upper voltage of block transformers and general application transformers of generating units connected to network of 110 kV and higher;

2) on the side of 110 kV transformers LV/110 kV, which are in the place where equipment, installations or networks of other entities are connected;

3) on the side of upper voltage of transformers or in line field with 110 kV and higher rated voltage, which are in the place of connection to final recipients;

4) in line fields with 110 kV and higher rated voltage of lines linked from the national electric power system to the electric power systems of other countries;

5) in line fields with 110 kV rated voltage of lines linked between electric energy distribution system networks;

6)  on clamps of generators in power plants rendering system services and in power plants requiring confirmation by the operator of the electric power grid concerning the amount of electric energy, necessary for claiming a certificate of origin in the sense of the Act.

With respect to the second group of requirements for the various connector groups, detailed specification of requirements for metering and accounting systems and measuring-control systems is provided in point II.2.

In all cases, the devices making up each metering and accounting system must be attested or type approved consistent with the requirements set for the given device. With respect to devices for which no attestation or type approval is required, the device must have an appropriate certificate confirming precision of measurement (calibration certificate). The interval between successive calibrations of such devices (except for current and voltage measuring transformers, which are subject to primary attestation) should not exceed the term of attestation of the active energy meter installed in the same metering and accounting system.

In accordance with points I.1.5 and II.3 of Annex 1 to the system regulation, the operator shall define detailed or additional technical requirements in the instructions, drafted on the basis of Article 9g of the Act, namely in Traffic and Operation of Distribution Network Instructions of given electric energy system operator. Requirements for specific instances of connecting production equipment to a network may differ from operator to operator. In this context, considering the practical experience of License Holders, the proposal is to request that given operators (to whose network the production equipment will be connected) define the conditions – technical requirements for connecting a given device or equipment group to the network.

According to § 6 section 1 of RES regulation, in a power plant burning biomass or biogas together with other fuels, classified as energy produced from renewable energy sources will be the part of electric energy or heat which corresponds to the share of chemical energy yielded by biomass or biogas in chemical energy of fuel used to generate energy, calculated on the basis of actual calorific value of such fuels, with reservation of § 9 section 1 according to the formula defined in the said regulation. According to section 2 of that article, registration and manner of calculating the quantity of electric energy or heat produced from renewable energy sources (EOZE) is to be conducted in accordance with the procedure of measuring, registering and calculating the quantity of energy produced in such sources, herein-after referred to as “accounting procedure”, for the given power plant. The accounting procedure shall be developed in accordance with:

  - Regulations governing measurements;

  - Norms defining requirements regarding competences of test or calibration laboratories, according to which tests of biomass or biogas will be conducted in laboratories with technical capabilities and skills in the area of accounting and testing procedures, documented to the satisfaction of these norms.

In the case of a power plant burning biomass or biogas together with other fuels:

- Measurements of mass represented by biomass in a solid state and solid fuel other than biomass involve measuring the mass of each of those fuels applied in the burning process;

- Measurements of mass represented by biomass in a liquid state or biogas and liquid or gas fuel other than biomass or biogas involve measuring the mass of each of those fuels applied in the burning process, using the direct method by measuring their mass (mass flow-meters) or using the indirect method by measuring the volume with correction for temperature, and with gas fuels, also for pressure of these fuels;

- Taking samples for testing the physical chemistry properties of the individual fuel types, necessary for calculating their calorific value, hereinafter referred to as “physical chemistry properties”, and measurement of the mass of those fuels is to be made at the same time and in the same place;

- Designating the physical chemistry properties of fuels should be consistent with the norms regarding properties of said fuels;

- In the absence of the norms referred to in point 4, for the given type of fuel used, designating the physical chemistry properties of that fuel is done according to methods validated to the satisfaction of the norms defining the requirements for test and calibration laboratories.

In cases where a power plant applies mixed secondary fuel, Article 7 of RES regulation calls for:

- Measuring the mass of the fuel provided for the burning process in the said power plant;

- Designating the combustion temperature and performing calculations of the calorific value of that fuel and samples of fuels from which the mixed secondary fuel has been composed;

- Registering the share of chemical energy of the biomass or biogas in the chemical energy of the mixed secondary fuel, consistent with Article 10.

One should also keep in mind that under Article 11 section 1, the place for taking measurements of the amount of electric energy produced from renewable energy sources, to meet the need for confirming the data referred to in Article 9e section 5 of the Act, are clamps of the:

- generator;

- photo-voltaic cell;

- the fuel cell in which the direct transformation of chemical energy into electric energy occurs.

If the metering and accounting devices on the clamps referred to in section 1 are not present, it is allowed to take the measurements at the place of connecting the renewable energy source to the network of the electric power system operator.

Other specific requirements regarding measurement, registration and manner of calculating the quantity of electric power or heat generated from renewable energy sources and guidelines as to the place for measuring the amount of electric power or heat generated from renewable energy sources for the purpose of meeting the requirement for validating the data referred to in Article 9e section 5 of the Act, are set forth in the RES regulation.

Considering the outline electrical schema (see following graph), one can distinguish the location of meters in the following places (designation consistent with the specimen application for a license, presented in Exhibit 1):

ZG	- metering electric energy on generator clamps;

ZPWE	- metering electric energy past drain-off points for own needs of the station;

GOSD	- metering electric energy at the point of connection with Power Grid Operator (OSE);

OSE	- Power Grid Operator, to whose grid the generating entity will be connected.

Graph 1. Oultline electrical schema

# Footnotes

group I – entities, whose equipment, installations and networks are connected directly to a network with rated voltage in excess of 110 kV;

group II – entities, whose equipment, installations and networks are connected directly to a network with 110 kV rated voltage;

group III – entities, whose equipment, installations and networks are connected directly to a network with rated voltage of more than 1 kV, but less than 110 kV;

group IV – entities, whose equipment, installations and networks are connected directly to a network with rated voltage of no more than 1 kV and connected power of no more than 40 kW or rated current of pre-meter protection in current line above 63 A;

group V - entities, whose equipment, installations and networks are connected directly  to a network with rated voltage of no more than 1 kV and connected power of no more than 40 kW or rated current of pre-meter protection in current line above 63 A;

group VI - entities, whose equipment, installations and networks are connected  to the network by a provisional connector which, under terms specified in the contract, will be replaced by a permanent connection, or entities, whose equipment, installations and networks are connected  to the network for a specified length of time, but not more than one year.

# Text boxes

G

ZPWE

G

OSD

Own needs

of power

plant

ZG

Direct recipients of generated

electric

energy

External power

Grid (OSE)